## Slide 1: Remote Monitoring of Nuclear Power Plants in Baden-Wuerttemberg - From Measurement to Emergency Protection NERIS Platform Workshop Bratislava, 6-8 February 2012
Thomas Wilbois
Walter Scheuermann
Christian Grimm
Matthias Hagmann
Ulrich Neff
Thomas Wilbois
Yongxiang Ren

## Slide 2: Geographical survey.
Monitoring Areas
Philippsburg (KKP)
Neckarwestheim (GKN)
Obrigheim (KWO)
Fessenheim (F)
Leibstadt, Beznau (CH)
Gundremmingen
Biblis
Cattenom
Mülheim-Kärlich
Source: Open Streetmap

## Slide 3
Duties and responsibilities of the System.
Monitoring of operational parameters and emissions of the plants perfomed by the supervisory authority and the assessor (TÜV)
Immission measuring network: ambient dose rate and aerosol concentrations, weather-stations (LUBW)
National and International data exchange
Dispersion calculation (prognostic and diagnostic): exposition of the public
Decision support tool for emergency protection :
  Radiological situation report
  Combined presentations of all data sources (incl. Calculations)
Simulation tool for the creation and implementation of excercises

## Slide 4: Basic System Architechture.
Power Plants
Regional
administration
KFÜ-Client
Terminal server
Ministry
KFÜ-Client
Local Database
Operating Company
KFÜ-Client
Meteorology
Measuring Teams
Immissions
External Networls
Phone based
Alerting system
Communikation
Server
Central
database
(Oracle RAC)
Dispersion
Calculation
Terminal server
On-call duty
KFUe
WebServer
Internet
LUBW Karlsruhe
Raw data Acquisition, Processing, Alerting Evaluations

## Slide 5: Supervision: Operational parameters and emissions.

## Slide 6
The KFUe radiation measuring network.
11 Aerosole stations located at
Plant sites (5)
Within the country (6)
Mobile (3)
2 Skylink Receivers (>100 km)
Königsstuhl & Feldberg
6 Shortlink Receivers (~10 km)
Close to each plant site (+1 mobile)
Ambient dose rate measuring
network (~110 stations)
Aerosole air concentrations

## Slide 7
All stations including data exchange.
    KFUe
    Measurements
    Bavaria,
    Gundremmingen
    Hesse, Biblis
    DWD
    BfS
    IRSN
    MADUK

## Slide 8: Dispersion calculation (IKE).
Dose calculations
, β submersion
Inhalation
Terristic radiation
Ingestion
Measurements
Forecasts
Thermal
Turbulence
Local wind regime
Large Scale Wind regime, Fallout, Washout

## Slide 9: Dispersion Calculation in the system.
Automatic and manual modes
Several methods for treatment of source term and meteorology
Diagnostic and prognostic calculations
Lagrange particle model based on
  Topography
  diagnostic Wind regime (3D)
  dispersion parameters (turbulent part)
  Models for dry and wet deposition
Dose module

## Slide 10
BfS-
Aerogamma
Measurement
teams
ABC-Explorers
Phases in nuclear emergency.
Stationary measurements
Dispersion calculations
Measures
Stationary measurements
Mobile measurements
Measures

## Slide 11
Measures and reference levels.
Measure | Dose | Reference level
Intake of iodine tablets | thyroid inhalation dose (7 days integration time including dose commitment) | 50 mSv (children, pregnant women) 250 mSv (adults)
Sheltering | Effective dose (children) (7 days integration time including dose commitment) | 10 mSv
Evacuation | Effective dose (children) (7 days integration time including dose commitment) | 100 mSv
§
§
§

## Slide 12: Providing Information for Emergency protection.
Weather forecasts and radar precipitation (DWD)
Stationary Measurements
Exchange of dispersion calculation results (and source terms)
Import of ABC-Explorer data, manual & Insitu-Measurements
Aerogamma data of the BfS
Interface to Electronic Situation Report System (ELD)

## Slide 13: Thank you. Questions?
Flyer available
http://www.um.baden-wuerttemberg.de/servlet/is/62324/
Application of the ABR to the Fukushima accident:
ATW, June 2011
Same system is in operation at
  Rhineland-Palatinate, Saarland
  KHG (on behalf of the operating companies)